Department of Public Administration   -   Maintenance Operations

Architecture, Facility Management Services and Street Light Utility

1532 West Michigan Street    •    Duluth, Minnesota    •    55806

218-730-5730  •  FAX 218-723-3560

tgroshong@duluthmn.gov

May 13, 2011

ADDENDUM NO. 1 - Bid # 11-16DS	CITY HALL ELEVATOR MODERNIZATION.

Project Number:	0907-Rebid

TO ALL BIDDERS:

This ADDENDUM is issued to modify, interpret or supplement the bidding documents and is hereby made a part of the bidding documents.  Please attach this ADDENDUM to the Project Manual in your possession, make the following modification to your Bid and acknowledge receipt of this ADDENDUM on your Bid Form.

GENERAL:

1.	The consultant's address and contact information is listed incorrectly. Please make note of the 	current address and contact:    	Elevator Advisory Group, Inc.

14530 Pennock Avenue, Suite 104

Apple Valley, Minnesota  55124

Attention: Kathy Markwell - Email: KMarkwellEAG@aol.com

Telephone:  (952) 432-4443

SPECIFICATIONS:

1.	The following plan holders are on record as of this date:

Laggerquist Elevators. – 302 West Superior Street, Suite 508 Lonsdale Bldg., Duluth, MN 55802

Schindler Elevator Corp., 301 West First Street, Duluth, MN 55802

Thyssen Krupp Elevator, 4511 West First Street, Duluth, MN 55807

Minnesota Elevator, Inc., 19336 – 607th Avenue, Mankato, MN 56001

Otis Elevator Co.,409 West  Michigan Street, Duluth, MN 55802

United States Elevator, 1275 Bloomfield Ave #9 Unit #81, Fairfield, NJ 07004

Amendola Builder's Inc., 405 East Superior Street, Duluth, MN 55802

Johnson Wilson Constructors, 4431 West Michigan Street, Duluth, MN 55807

- BID TIME: EXTENSION - There is a need and desire to extend this bid time. The new bid date and time is as follows:

- BID DUE DATE:  The bid due date has been extended from May 17th to Thursday, May 26th, 2011 at 2:00 PM - CST.

- APPROVALS:

- A.	Division 14, 1.04 Quality Assurance, B. Products: Smart Rise Controllers is an acceptable manufacturer.

- 4.	DECOMMISSION ELEVATORS:

Please note the following changes and/or modifications to the project specifications for the modernization of the elevators in the CITY HALL located in Duluth, Minnesota:

- It is the intent of this project scope to remove and appropriately discard the existing elevators, rails, guides, controls and ancillary items associated with same so that floor infill and modernization work can occur. Intended use is for these spaces to be used by City MIS department. Power to the space is not intended for this contract, save for the specified lighting requirement. It is intended that the electrical contractor shall research, identify and make connection onto the closest existing circuit to provide power to same. Fixture specified and shown is a motion sensor light and requires no switch.

B.	2.01 SCOPE OF WORK

The two traction passenger elevators (#1 and #2) shall be decommissioned by the following means:

(ADD)

- Install concrete floors (minimum of 150lb sq/ft) at each level of

both hoistways.  At the lowest landing, provide steel grating floors in lieu of concrete (in both hoistways)

- Provide and install lockable, 2 hour rated steel swing doors and jambs at each level in both hoistways.

Remove the following

(ADD)

- Remove both elevators in their entirety including ALL related equipment and parts from their respective machine rooms and hoistways.

- Remove ALL hoistway doors and tracks.

If you should notice any discrepancies, have any questions, comments, or request clarification – please feel free to contact our office.

Kathy Markwell

Elevator Advisory Group, Inc.

14530 Pennock Avenue, Suite 104

Apple Valley, MN  55124

Telephone: (952) 432-4443

KMarkwellEAG@aol.com

- 5.	MODERNIZATION ELEVATORS (as provide by Elevator Advisory Group):

Please note the following changes and/or modifications to the project specifications for the modernization of the elevators in the CITY HALL located in Duluth, Minnesota:

- BID DUE DATE:  The bid due date has been extended from May 17th to Thursday, May 26th, 2011 at 2:00 PM - CST.

B.	Division 14; 2.01 MATERIALS & PRODUCT APPLICATIONS:

A. Data Outline - Elevators #1 & #2

Traveling Cables: ADD: New - with One (1) Coaxial Cable

Remove: New with Four (4) Coaxial Cable

C.	Division 14; 2.01 MATERIALS & PRODUCT APPLICATIONS:

A. Data Outline - Elevators #1 & #2

Governors - Car: ADD: New - Hollister Whitney

NewTail Sheave

(ADD) PIT LADDER:	Remove and replace with NEW code-compliant pit ladder

(ADD) GOVERNOR TENSION SHEAVES:  	Provide NEW

D.	2.53 CAB, 3.,  e.

TOE KICK (replace with) GUARD – Stainless Steel   (replace with) CODE COMPLIANT

E.	2.54 RELATED WORK, A. Work By Owner (replace with) ADDITIONAL WORK 	INCLUDED

F.	2.54 RELATED WORK, A. ADDITIONAL WORK INCLUDED,

2. Any modificationto existing shaftway to provide a legal shaftway in compliance with the latest code requirements, (ADD) including but not limited to setbacks and ledges.

7. Any modifications to machine room to provide adequate and code compliant access to same.

(ADD) Stabilize and re-inforce the existing ship ladder to machine room to provide safe and convenient access.  Provide a legal landing with steps outside of machine room.

(ADD) Provide adequate access to machine room for removal and replacement of any equipment, including cranes.  Upon completion of project, access shall have a code-compliant, lockable door installed.

- 2.54 RELATED WORK, . WORK BY ELEVATOR CONTRACTOR: (REMOVE 	THE FOLLOWING)

  - Contractor must assist Owner with coordination of WORK BY OWNER (as described in 1.13 Related Work – WORK BY OWNER)

7.  Painting of machine room (ADD) and PIT floors with good grade

of grey enamel paint.

G.	Elevator Equipment Room: (See attached Controller Power Report for BTU Generation. 	Specified cooling unity shall be sized to meet the loads as indicated and shown in this 	report. Currently listed as 9,013 BTU's. Size for 10,000 BTU's.

H.	Division 16 Electrical Performance Specification. Clarification: Please delete any and all 	references to include Harrison Project. Substitute City Hall for same. It is the intent of 	this performance specification to provide minimum standards to the work as it applies to 	this project. Not all items listed are included or contained with in this project. It is 	intended that the 	licensed electrical contractor provide all necessary and required items 	shown or specified for the elevator supplier and elevator equipment. It is their 	responsibility to coordinate any and all required electrical need to equipment, 	motors, controls, devices, switches, disconnects or any other components necessary 	to 	provide the Owner with a licensed, certified and fully operational elevator. 	Coordinate 	any and all low voltage and life safety enunciators, devices and panels. It is also the 	intent of these specifications and drawings to have all wiring, conduits and feeds 	concealed within any finished space. Exceptions are machine rooms, tunnels, chases, 	above ceilings and control rooms, closets or cabinets. Said feeds can be in code 	compliant conduit securely fastened to the substrate.

DRAWINGS:  General:  The drawings included with this project depict work required to service the elevators and provide minimum detailing for work necessary to install same. It is intended that these documents act as a performance guideline and it is expressly understood that the contractor(s) shall perform any required field adjustments on site to meet the existing conditions. References to product and method are intended to be minimum characteristics which meet or exceed current code. Any deviation or field adjustment must do same.

Floor Infill Detail: 4:A1 - Grated Floor Infill at Ground Floor. Ground Floor references the elevators last stopping point. On the decommissioned elevators, all floors and stops are to receive infill..

- End Addendum 1

- Sincerely,

- Terry L. Groshong, AIA

City Architect